# PHE-31 Permit, Handover and Confined Space Notes

Prepared for maintenance workpack filing. Use as source records only; do not treat narrative notes as quantified measurements.

# Permit and isolation references

| record_id | asset_tag | date | record_type | field_name | source_value | unit | source_record_ref | note |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PTW-001 | PHE-31 | 2026-05-12 | permit | permit_reference | PTW-31-0512-HYD | text | permit book | hydrotest permit |
| PTW-002 | PHE-31 | 2026-05-12 | loto | loto_reference | LOTO-31-0512-A | text | lock box tag | hot side isolation |
| PTW-003 | PHE-31 | 2026-05-12 | loto | loto_reference |  | text | handover sheet | LOTO reference not written for hot outlet blind |
| PTW-004 | PHE-31 | 2026-05-12 | confined space | confined_space_entry | not required | text | permit book | external work only |
| PTW-005 | PHE-31 | 2026-05-13 | closeout | closeout_signature |  | text | handover sheet | closeout signature missing at end of night shift |

# Shift handover notes

| record_id | asset_tag | date | shift | note_type | source_value | unit | note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SH-001 | PHE-31 | 2026-05-12 | day | observation | small weep at lower right corner | text | seen during initial hydrotest hold |
| SH-002 | PHE-31 | 2026-05-12 | day | observation | chalk mark on upper tie bar | text | descriptive mark only |
| SH-003 | PHE-31 | 2026-05-12 | night | observation | pressure held after second pass | text | no numeric pressure recorded in note |
| SH-004 | PHE-31 | 2026-05-13 | night | condition | floor dry under drain side | text | visual note |
| SH-005 | PHE-31 | 2026-05-13 | night | handover_status | not signed | text | return-to-normal handover missing signature |

# Gauge and tool handover notes

| record_id | asset_tag | date | tool_or_gauge | field_name | source_value | unit |
| --- | --- | --- | --- | --- | --- | --- |
| GT-001 | PHE-31 | 2026-05-12 | PG-31-HT-02 | gauge_range | 0-16 | bar |
| GT-002 | PHE-31 | 2026-05-12 | PG-31-HT-02 | calibration_date | 2026-05-18 | date |
| GT-003 | PHE-31 | 2026-05-12 | TW-31-02 | tool_condition | sealed case intact | text |